## LSICALC
Langelier's and Ryznar's Indices
* | * | * | * | * | * | *
Measured Water Characteristics
Calcium (MG/L as CaCO3) |  |  |  | 48
pH |  |  |  | 8.62
Temperature (Degrees Celcius) |  |  |  | 20
Alkalinity (MG/L as CaCO3) |  |  |  | 160
Total Dissolved Solids(MG/L) |  |  |  | 1064
* | * | * | * | * | * | *
Calculated Langelier's Index and Ryznar's Stability Index
Langelier's Saturation Index |  |  |  | 0.34843
Ryznar's Stability Index |  |  |  | 7.9
If the LSI index is negative or the Ryznar >6.0 calcium carbonate is soluble and deposition unlikely.
If the LSI index is positive or the Ryznar < 6.0 calcium carbonate deposition is likely.
* | * | * | * | * | * | *
Calculated Data
Ionic Strength |  |  |  | 0.0266
Activity Coefficient(m) |  |  |  | 0.85258
Activity Coefficient(d) |  |  |  | 0.52838
Ca(moles/L) |  |  |  | 0.00048
Alk(moles/L) |  |  |  | 0.0016
pK2 |  |  |  | 10.3782
K2 |  |  |  | 4.1856e-11
K2' |  |  |  | 7.9217e-11
pK2' |  |  |  | 10.1012
pKs |  |  |  | 8.2666
Ks |  |  |  | 5.4125e-09
Ks' |  |  |  | 1.9387e-08
pKs' |  |  |  | 7.7125
pCa |  |  |  | 3.3188
pHs |  |  |  | 8.2716
Customer:
Site : Wichita, KS
Sample Identification: Air Stripper Inlet